
Fault Condition Eleven Report

Fault condition eleven of ASHRAE Guideline 36 is an AHU economizer + mechanical cooling mode only with an attempt at flagging conditions where the outside air temperature is too low for 100% outside air AHU operating mode. Fault condition Eleven equation as defined by ASHRAE:




## Dataset Plot



## Dataset Statistics

* Total time in days calculated in dataset: 322.0
* Total time in hours calculated in dataset: 7727.983333333334
* Total time in hours for when fault flag is True: 0.8833333333333333
* Percent of time in the dataset when the fault flag is True: 0.02%
* Percent of time in the dataset when the fault flag is False: 99.98%
* Calculated motor runtime in hours based off of VFD signal > zero: 3061.08

## Time-of-day Histogram Plots



* When fault condition 11 is True the average AHU mix air is 45.87 in °F and the supply air temperature is 55.04 in °F.

# Summary Statistics filtered for when the AHU is running

### Supply Air Temp Setpoint

* count 1.836650e+05  
  mean 5.504000e+01  
  std 2.131634e-14  
  min 5.504000e+01  
  25% 5.504000e+01  
  50% 5.504000e+01  
  75% 5.504000e+01  
  max 5.504000e+01  
  Name: AHU: Supply Air Temperature Set Point, dtype: float64

### Outside Air Temp

* count 183665.000000  
  mean 47.087935  
  std 22.141181  
  min -14.236000  
  25% 32.720000  
  50% 51.700000  
  75% 63.536000  
  max 90.140000  
  Name: AHU: Outdoor Air Temperature, dtype: float64

## Suggestions based on data analysis

* The percent True metric that represents the amount of time for when the fault flag is True is low inidicating the AHU components are within calibration for this fault equation Ok.

Report generated: Sat Apr 1 13:59:54 2023